UTILITIES ENERGY OPTIMIZATION

Platform Blueprint  ·  Universal Use Case Framework

Covering: Boilers  ·  Chillers  ·  Cooling Towers  ·  Compressed Air  ·  Steam Networks

Reactors  ·  Furnaces  ·  Heat Exchangers  ·  Cogeneration (CHP)  ·  Power Distribution

| Platform Vision | Optimizer Strategy | Delivery Model |
| --- | --- | --- |
| Replace siloed, hardcoded tools with a configurable Python product adaptable to any utility asset | MINLP (Pyomo/SCIP) as baseline; Bayesian Optimization surrogate for noisy/unknown systems | Two philosophies: Gen AI assisted onboarding + Config-driven deterministic pipeline |

Version 1.0  |  Industrial Energy Optimization Product  |  2025

1. Strategic Context: Why Utilities Energy Optimization?

Industrial plants are losing up to 67% of input energy before it reaches its intended purpose — through fouling heat exchangers, poor combustion control, leaking compressed air, and failing steam traps. This platform targets that waste systematically across every utility asset type.

The core problem: Each utility system — boilers, chillers, compressors, cooling towers — is optimized in isolation. When a chiller chases its own efficiency target, it can conflict with the steam header or cooling tower, creating plant-wide inefficiencies. This platform treats the entire site as a single energy ecosystem.

| Utility System | Typical Energy Loss | Optimization Lever | Savings Potential |
| --- | --- | --- | --- |
| Steam / Boiler System | 15–25% via flue gas, steam trap failures | Fuel-air ratio, load distribution, condensate recovery | 10–20% |
| Chiller Plant | 20–30% at part load | Chiller staging, condenser water setpoints, VSD control | 15–30% |
| Cooling Tower | 10–15% fan/pump energy waste | Fan speed, approach temperature, wet-bulb tracking | 10–20% |
| Compressed Air | 20–30% through leaks and pressure drops | Header pressure, compressor sequencing, demand profiling | 15–25% |
| Furnace / Fired Heater | 5–15% excess air, poor heat distribution | Excess O2 control, zone setpoints, feed rate optimization | 5–15% |
| Heat Exchangers | Fouling = 20% capacity loss over time | Fouling factor tracking, cleaning schedule, bypass control | 5–10% |
| Cogeneration (CHP) | Sub-optimal dispatch between GTG/boiler/STG | Load-sharing optimization, steam extraction balance | 10–20% |

2. Universal Use Case Library

Each use case in the platform is defined by a case_id in the CONFIG_TABLE. The same 8-pipeline Kedro architecture runs all of them — only the configuration changes.

## 2.1  Use Case 1: Boiler Optimization

Objective: Minimize fuel consumption (gas/oil) while meeting steam demand headers (HPS/MPS/LPS) with minimum downtime.

| PI Tag Category | Example Tags | Inferred KPIs |
| --- | --- | --- |
| Combustion | Flue_O2_%, Flue_CO_ppm, Stack_Temp_C, Fuel_Flow_GJ_Hr | Excess_Air_%, Combustion_Efficiency_% |
| Steam Generation | Steam_Flow_T_Hr, Steam_Pressure_bar, Steam_Temp_C | Boiler_Efficiency_%, Heat_Rate_GJ_T |
| Feedwater | FW_Temp_C, FW_Flow_T_Hr, Blowdown_Flow_T_Hr | Blowdown_Rate_%, Makeup_Water_Cost |
| Load | HPS_Demand_T_Hr, MPS_Demand_T_Hr, LPS_Demand_T_Hr | Total_Steam_Demand, Boiler_Load_% |

Boiler Optimizer Variables & Constraints

- VARIABLES: Boiler_N_Status (binary), Boiler_N_Load_T_Hr (continuous), Excess_Air_Setpoint_% - OBJECTIVE: Minimize SUM(Fuel_Cost_N * Boiler_N_Load) across all active boilers - CONSTRAINTS: Total_Steam_Gen >= Total_Steam_Demand; Boiler_Load between MinLoad and MaxLoad when ON - INTEGER LOGIC: Minimum number of boilers ON to meet demand; startup cost penalty for mode changes - SOLVER: Pyomo + SCIP (open-source MINLP) — globally optimal for non-convex combustion curves

## 2.2  Use Case 2: Chiller Plant Optimization

Objective: Minimize total kWh consumed across chiller plant (chillers + cooling tower fans + condenser pumps + chilled water pumps) while meeting cooling load.

| PI Tag Category | Example Tags | Inferred KPIs |
| --- | --- | --- |
| Chiller Performance | CH_N_Power_kW, CH_N_COP, CH_N_ChW_Sup_T, CH_N_ChW_Ret_T | CH_N_Part_Load_Ratio, System_COP |
| Cooling Tower | CT_Fan_Speed_%, CT_App_Temp_C, WB_Temp_C, CW_Sup_T, CW_Ret_T | CT_Efficiency_%, Approach_Temperature |
| Pumping | ChWP_N_Speed_%, CWP_N_Speed_%, ChWP_N_Flow_m3_Hr | Pump_Power_kW, System_Delta_P_bar |
| Demand | Building_Load_kW, Zone_Temp_C, Outdoor_DB_C, Outdoor_WB_C | Cooling_Load_Tons, PLR_System |

Chiller Optimizer Variables & Constraints

- VARIABLES: CH_N_Status (binary), CH_N_ChW_Supply_Setpoint (continuous), CT_Fan_Speed_% (continuous) - OBJECTIVE: Minimize Total_Plant_kWh = SUM(CH_N_kW + CT_N_kW + CWP_N_kW + ChWP_N_kW) - CONSTRAINTS: Chilled water supply temperature must meet demand; minimum flow through each active chiller - BAYESIAN LAYER: COP-vs-PLR curves are non-linear and equipment-specific — Bayesian surrogate learns these - WEATHER INTEGRATION: Wet-bulb temperature feeds constraint engine dynamically for cooling tower control

## 2.3  Use Case 3: Cooling Tower Optimization

Objective: Minimize cooling tower fan and pump energy while maintaining condenser water return temperature within acceptable bounds.

| PI Tag | Description | Optimization Role |
| --- | --- | --- |
| CT_Inlet_WB_Temp_C | Ambient wet-bulb temperature | Primary parameter — defines minimum achievable CW temp |
| CT_Fan_N_Speed_% | Individual cell fan speed (VFD) | Decision variable — reduce fan power at favorable WB |
| CT_CW_Supply_Temp_C | Condenser water to chillers | Constraint — must not exceed chiller condenser limit |
| CT_Drift_Loss_m3_Hr | Water loss to atmosphere | Environmental constraint — water conservation |
| CT_Cell_N_Status | Cell enable/disable (binary) | Integer variable — minimum cells to meet load |

## 2.4  Use Case 4: Compressed Air System Optimization

Objective: Minimize total compressed air generation cost by optimally sequencing compressors and minimizing system pressure setpoints while meeting all demand points.

| PI Tag Category | Example Tags | Inferred KPIs |
| --- | --- | --- |
| Compressor Performance | COMP_N_Power_kW, COMP_N_Pressure_bar, COMP_N_Flow_Nm3_Hr | COMP_N_Specific_Power_kWh_Nm3, Load_% |
| System | Header_Pressure_bar, Total_Flow_Nm3_Hr, Leakage_Flow_% | Leakage_Cost_USD_Hr, System_Efficiency_% |
| Demand | Process_Air_Demand_Nm3_Hr, Critical_Pressure_bar | Demand_Profile, Peak_Demand_Factor |

Compressed Air Key Optimization Insight

- Every 1 bar reduction in system header pressure saves approximately 7% compressor energy - Compressor sequencing (lead/lag assignment) is a classic integer programming problem — MINLP is the natural solver - Leakage estimation is an inferred tag: Leakage_% = (Unloaded_Run_Time / Total_Run_Time) * 100 - Peak demand charge avoidance is an objective term: penalize configurations that create demand spikes

## 2.5  Use Case 5: Cogeneration (CHP) Dispatch Optimization

Objective: Optimally dispatch gas turbines, HRSGs, supplementary boilers, and steam turbine generators to minimize total utility cost (fuel + power import) while meeting all steam and power demands.

| PI Tag Category | Example Tags | Inferred KPIs |
| --- | --- | --- |
| Gas Turbine | GTG_N_Power_MW, GTG_N_Fuel_GJ_Hr, GTG_N_Exhaust_Temp_C | GTG_N_Efficiency_%, Heat_Rate_GJ_MWh |
| HRSG / Boiler | HRSG_N_Steam_T_Hr, HRSG_N_Duct_Firing_GJ_Hr | HRSG_N_Steam_Efficiency_% |
| Steam Headers | HPS_Flow_T_Hr, MPS_Flow_T_Hr, LPS_Flow_T_Hr, HPS_Pressure_bar | Header_Balance_T_Hr, Steam_Letdown_Loss |
| Power | Grid_Import_MW, Grid_Export_MW, Site_Power_Demand_MW | Net_Power_Cost_USD_Hr |

## 2.6  Use Case 6: Heat Exchanger Network Optimization

Objective: Detect fouling early, optimise bypass and flow routing, and recommend cleaning schedules to restore heat transfer efficiency.

| PI Tag | Description | Inferred KPI |
| --- | --- | --- |
| HX_N_Hot_In_T / Hot_Out_T | Hot side inlet/outlet temperatures | HX_N_Duty_MW = Flow * Cp * (Hot_In - Hot_Out) |
| HX_N_Cold_In_T / Cold_Out_T | Cold side inlet/outlet temperatures | HX_N_U_Value = Duty / (Area * LMTD) |
| HX_N_Flow_m3_Hr | Shell/tube side flow | HX_N_Fouling_Factor = 1/U_actual - 1/U_clean |
| HX_N_DP_bar | Differential pressure across exchanger | HX_N_Cleaning_Urgency_Score (0–100) |

Heat Exchanger Optimization Engine

- Fouling factor is computed as a calculated tag from U-value degradation over time - A cleaning urgency score (inferred KPI) ranks exchangers by savings potential vs cleaning cost - Optimizer recommends optimal bypass fractions and cleaning sequence to maximise network duty - Bayesian Optimization is ideal here: fouling curves are highly non-linear and asset-specific

3. Solver Selection Framework: Beyond Gekko

Based on current research, the optimal solver choice depends on the use case characteristics. The following framework guides selection across all utility optimization problems:

| Use Case | Problem Type | Recommended Solver | Why |
| --- | --- | --- | --- |
| Boiler Load Dispatch | MINLP (binary ON/OFF + continuous load) | Pyomo + SCIP | Global optimum, free, handles non-convex combustion curves |
| Chiller Plant | MINLP with non-linear COP curves | Pyomo + SCIP + Bayesian surrogate | COP-PLR curves learned from historian; SCIP solves staging |
| Cooling Tower | Continuous NLP with weather parameters | Pyomo + IPOPT | Convex for given WB temperature; fast, reliable |
| Compressed Air | MILP (compressor sequencing) + NLP | Pyomo + BARON (if licensed) / SCIP | Non-convex efficiency curves; integer staging |
| CHP Dispatch | Large-scale MINLP | Pyomo + BARON or Gurobi | Complex multi-unit dispatch; commercial solver justified |
| Heat Exchanger | Continuous NLP + scheduling | Bayesian Optimization (BoTorch) | Noisy fouling signals; black-box U-value degradation |
| Any (warm-started) | Any with rich historical data | ML surrogate + gradient optimizer | 10+ years of data available — surrogate captures nonlinearities |

Recommended Solver Stack for This Platform

- TIER 1 (Default): Pyomo + SCIP — open-source, globally optimal, Python-native, handles all MINLP cases - TIER 2 (Data-rich cases): BoTorch Bayesian Optimization — trains on historian data, handles noisy/non-linear systems - TIER 3 (Enterprise): Pyomo + BARON or Gurobi — maximum solver power for complex CHP/multi-unit dispatch - FUTURE: Physics-Informed Neural Network (PINN) surrogate — train on 10+ years of data, embed process constraints in network - AVOID: Gekko APOPT for production-scale problems — convergence unreliable for large non-convex MINLP

4. Universal Tag & Config Schema

All use cases share a single CONFIG_TABLE schema. The case_id field is the only thing that changes when deploying to a new asset or site.

| Field | Type | Description | Example (Boiler) | Example (Chiller) |
| --- | --- | --- | --- | --- |
| case_id | VARCHAR | Unique use case identifier | BOILER_SITE_A_01 | CHILLER_PLANT_B_01 |
| tag_id | INT | Auto-increment PK | 1 | 1 |
| asset_type | VARCHAR | Utility asset class | BOILER | CHILLER |
| tag_name | VARCHAR | Internal system name | Flue_O2_Pct | CH_1_COP |
| pi_tag_name | VARCHAR | AVEVA PI historian tag | TI_FG_O2_001 | AI_CH1_COP |
| tag_type | ENUM | pi / calculated / constant / parameter | pi | calculated |
| formula | VARCHAR | df.eval() expression (if calculated) | NULL | (CH_1_Evap_kW / CH_1_Power_kW) |
| unit | VARCHAR | Engineering unit | % | - |
| min_value | FLOAT | Physical lower bound for imputation | 0.5 | 0.1 |
| max_value | FLOAT | Physical upper bound for imputation | 25.0 | 12.0 |
| imputation_method | VARCHAR | clip / ffill / interpolate / model | clip | ffill |
| optimizer_role | ENUM | variable / parameter / constraint / objective / kpi | parameter | kpi |
| lb | FLOAT | Optimizer lower bound (if variable) | NULL | NULL |
| ub | FLOAT | Optimizer upper bound (if variable) | NULL | NULL |
| active | BOOL | Enable/disable tag without deletion | TRUE | TRUE |

5. Universal Pipeline Architecture (Kedro)

The same 8 micro-pipelines run every use case. Configuration is injected via load_config_from_db(case_id). No Python code changes are needed when adding a new asset.

| Pipeline | Key Nodes | Butamer / Reactor | Boiler | Chiller | Cooling Tower |
| --- | --- | --- | --- | --- | --- |
| 1. Ingestion | load_pi_data, map_tags | Reactor feed, bed DTs | Flue gas, steam flows | COP, load sensors | Fan speed, WB temp |
| 2. Preprocessing | remove_outliers, validate_schema | DT spike removal | O2/CO range check | COP > 12 → outlier | Approach temp bounds |
| 3. Feature Engineering | DAG + df.eval() | Lead_Reactor_Activity | Combustion_Efficiency | System_COP, PLR | CT_Efficiency_% |
| 4. Imputation | ffill, clip, interpolate | Thermocouple dropout → ffill | O2 sensor → default 3% | Power meter → interp | WB sensor → model |
| 5. Constraint Builder | load_constraints | Reactor temp limits | Min/max steam demand | Min chilled water T | Max CW return T |
| 6. Objective Builder | define_objective | Min fuel * activity pen | Min fuel cost | Min total plant kWh | Min fan+pump kWh |
| 7. Optimization | Pyomo solver node | SCIP/MINLP | SCIP/MINLP | SCIP + Bayes | IPOPT/NLP |
| 8. Reporting / ODS | join, opportunity, write | Actual vs Optimum setpoints | Fuel saving USD/Hr | kWh saving | Energy saving kWh |

6. Inferred Tag Library by Use Case

Inferred tags are calculated from PI tags using the formula engine. They represent the engineering KPIs that describe asset health and performance — and feed the objective function and constraints.

| Asset | Inferred Tag | Formula (df.eval style) | Engineering Meaning |
| --- | --- | --- | --- |
| Boiler | Combustion_Efficiency_% | (1 - (Flue_Temp - Ambient_T) * 0.0063 - O2_loss) * 100 | Heat captured as steam / total heat input |
| Boiler | Blowdown_Cost_USD_Hr | Blowdown_Flow * (Steam_Enthalpy - FW_Enthalpy) * Fuel_Price / 1000 | Energy wasted via boiler blowdown |
| Chiller | System_COP | Total_Evap_kW / Total_Compressor_kW | Cooling output per unit electrical input |
| Chiller | Part_Load_Ratio | Actual_Cooling_Load / Chiller_Rated_Capacity | How hard the chiller is working (0–1) |
| Cooling Tower | Approach_Temperature_C | CW_Supply_Temp - Wet_Bulb_Temp | Delta between CW and WB — lower is better |
| Cooling Tower | CT_Efficiency_% | (WB_Temp - CW_Supply_T) / (WB_Temp - CW_Return_T) * 100 | How effectively tower rejects heat |
| Compressed Air | Specific_Power_kWh_Nm3 | Compressor_Power_kW / Flow_Nm3_Hr | Energy intensity of compressed air generation |
| Compressed Air | Leakage_Flow_% | Unloaded_Time_Hr / Total_Time_Hr * 100 | Fraction of capacity lost to leaks |
| CHP | GTG_Heat_Rate_GJ_MWh | Fuel_Flow_GJ_Hr / Power_Output_MW | Efficiency of gas turbine: lower is better |
| Heat Exchanger | Fouling_Factor_m2K_W | 1/U_Actual - 1/U_Clean_Design | Thermal resistance from fouling; drives cleaning decision |
| Heat Exchanger | Cleaning_Urgency_Score | (Fouling_Factor / Max_Fouling) * 100 | 0–100 score; >80 triggers cleaning recommendation |
| Reactor (Butamer) | Lead_Reactor_Activity_% | (Lower_Bed_DT + Middle_Bed_DT + Upper_Bed_DT) / Feed * 100 | Catalyst activity estimated from temperature rise pattern |

7. Deployment Roadmap: From Single Use Case to Full Platform

| Phase | Scope | Deliverable | Timeline |
| --- | --- | --- | --- |
| Phase 1: Foundation | Core Kedro scaffold, CONFIG_TABLE, tag schema, mock PI loader | Working pipeline skeleton + DB schema | Weeks 1–2 |
| Phase 2: First Use Case | Deploy Boiler Optimization (simplest MINLP) | End-to-end pipeline for boiler case_id | Weeks 3–5 |
| Phase 3: Second Use Case | Chiller Plant with Bayesian surrogate layer | Two use cases; Pyomo + SCIP + BoTorch | Weeks 6–8 |
| Phase 4: Gen AI Onboarding | LLM tag extractor, classifier, formula validator, Streamlit review UI | Engineer can onboard new case in < 1 day via diagram upload | Weeks 9–10 |
| Phase 5: Remaining Cases | Cooling Tower, Compressed Air, CHP, Heat Exchanger | Full 6-use-case library deployed on same infrastructure | Weeks 11–14 |
| Phase 6: Site-Wide Optimizer | Multi-asset joint optimizer: boiler + chiller + CHP solved simultaneously | Whole-plant energy cost minimization | Weeks 15–18 |
| Phase 7: Productionization | PI live connection, monitoring dashboards, alerting, retraining | Production-ready SaaS/on-premise product | Weeks 19–22 |

Golden Rule: One config change deploys to any utility. One pipeline runs all use cases.

Utilities Energy Optimization Blueprint  ·  v1.0  ·  2025