EO Pipeline — Demo Outline

Block 1: PI Tag Ingestion  ·  Block 2: Inferred Tag Calculation

Architecture · Data Flow · Code Logic · GenAI Integration Points

Prepared for Product Team Demo  |  SABIC U&O  |  EO Optimization Pipeline

| Dimension | Block 1 — PI Tag Ingestion | Block 2 — Inferred Engine |
| --- | --- | --- |
| Data source | PI Historian (PI-DA.sabic.com) — 899 PI tags registered | Feature file inferred_details table — 2,863 formulas |
| In EO_input_data.xlsx | 4,320 hourly rows × 438 columns ¦ Jun 2024 → Nov 2024 | Not in PI — computed from PI values at runtime |
| Snapshot used | 2024-11-29 00:00:00 (latest valid row) | Same snapshot — evaluated against PI context |
| Tags available (Nov run) | 437 of 899 PI tags (PI Web API would give all 899) | 2,239 of 2,863 inferred tags successfully evaluated |
| Kedro nodes count | 3 atomic nodes | 5 atomic nodes (+ 2 shared utilities) |
| Processing time (demo) | < 0.5 seconds | ~15 seconds (DAG build + 2,239 evaluations) |

# Block 1 — PI Tag Ingestion Pipeline

Micro-pipeline: ingestion/nodes.py  |  Kedro stage 01 of 08

## 1.1  What Is a PI Tag and Why Do We Need This Block?

Every sensor on the SABIC site — pressure transmitters, temperature gauges, flow meters, valve positions, motor status relays — streams its value in real-time into the OSIsoft PI Historian database. Each data point is identified by a PI tag address, which follows the naming convention:

UN.UO.70PI0012A.PV   →  HP Steam Pressure (bar g)

UN.UO.70TI0007.PV    →  HP Steam Temperature (°C)

UN.UO.71FI1001.PV    →  BFW Flow to Boiler 1 (kg/h)

The PI Historian stores these as a time-series. For optimization, we do not need the live stream — we need one clean snapshot: the 1-hour averaged value at the current time, representing the plant state right now. This block retrieves that snapshot, validates it, and converts it into a Python dictionary that every downstream stage can query by tag name.

| INPUT | What goes into this block |
| --- | --- |

| Input | Source | Format | Key content |
| --- | --- | --- | --- |
| PI Historian connection | osisoft.pi / PI Web API (production) Excel mock (demo) | Connection object / xlsx file | PI server address from pipeline_macros: pi_rootpath = \\PI-DA.sabic.com |
| EO_input_data.xlsx | PI export (mock snapshot for demo) | 4,320 rows × 438 columns Index = hourly timestamps | One row per hour, Jun–Nov 2024 437 tag columns with float values |
| tag table (feature file) | EO_UN_FF_Rev_14.xlsx sheet: tag | 3,761 rows Columns: tag_name, pi_name, tag_type, description | 899 PI tags with their PI server addresses 2,862 inferred tags (no PI address) |
| pipeline_macros (feature file) | EO_UN_FF_Rev_14.xlsx sheet: pipeline_macros | 9 rows | data_pull_window = 1d data_pull_timeinterval = 1h pi_rootpath = \\PI-DA.sabic.com |
| case_configuration_portal | EO_UN_FF_Rev_14.xlsx sheet: case_configuration_portal | 107 rows Columns: tag_name, default_value, lolo, hihi, switch codes | Quality rules for 107 critical tags: NaN switch, OOB switch, stuck switch, default values, LOLO/HIHI bounds |

| OUTPUT | What comes out of this block |
| --- | --- |

| Output | Format | Size (Nov 2024) | What it represents |
| --- | --- | --- | --- |
| snapshot_validated | pd.Series (tag_name → float) | 437 entries | One clean float value per PI tag at the selected timestamp. Bad values replaced with CCP defaults. |
| snapshot_ts | string | 1 value | "2024-11-29 00:00:00" — the timestamp of the selected row |
| ctx_actual (built from snapshot) | Dict[str, float] | 874 entries (437 × 2) | Every PI tag stored twice: as tag_name AND as tag_name_actual. Enables _actual/_optimum dual-context downstream. |
| ccp_issues | List[Dict] | 3 issues (Nov run) | Audit log of what was corrected: which tag, what was wrong, what it was replaced with. |

| CODE | The three Kedro nodes — how they work |
| --- | --- |

### Node 1/3 — create_pi_connection

| Property | Detail |
| --- | --- |
| Function signature | create_pi_connection(pi_config: Dict) → Dict |
| Responsibility | Establish and return a connection handle to the PI Historian |
| Demo implementation | Returns a mock dict: {"source": "excel_mock", "status": "connected"} |
| Production swap | from osisoft.piwebapi import PIWebApiClient client = PIWebApiClient("https://PI-DA.sabic.com/piwebapi", useKerberos=True) |
| Why atomic? | Connection setup is separate from data retrieval — allows testing data fetch without a live PI server |

### Node 2/3 — fetch_pi_data

| Property | Detail |
| --- | --- |
| Function signature | fetch_pi_data(pi_conn, pi_data_path) → Tuple[pd.Series, str] |
| Responsibility | Load the PI data file, parse timestamps, return the latest valid row as a Series |
| Robustness | Tries 3 engines in sequence: openpyxl → xlrd → csv fallback. Auto-resolves Colab renamed files (e.g. "EO_input data (1).xlsx" → canonical name). |
| Key logic | df_raw.index = pd.to_datetime(index, errors="coerce") df_valid = df_raw[df_raw.index.notna()] snapshot = df_valid.iloc[-1] # most recent valid row |
| Production swap | Query PI Web API: GET /streams/recorded?startTime=*-1d&endTime=*&interval=1h Return last row of the interpolated response |
| Data facts | EO_input_data.xlsx: 4,320 rows × 438 columns ¦ Jun 2024 – Nov 2024 437 of 438 columns have non-null data in every row |

### Node 3/3 — standardize_columns

| Property | Detail |
| --- | --- |
| Function signature | standardize_columns(snapshot: pd.Series, tag_cfg: pd.DataFrame) → pd.Series |
| Responsibility | Rename PI-native tag names to the canonical names used by every formula in the feature file |
| Why needed? | PI stores boiler-specific energy as "Sp_En_BO_7104A" but the feature file references "Spec_En_Cons_BLR_1". Without this rename, the SEU formulas and inferred tag formulas cannot find the value. |
| Current alias map | Sp_En_BO_7104A → Spec_En_Cons_BLR_1 Sp_En_BO_7104B → Spec_En_Cons_BLR_2 Sp_En_BO_7104C → Spec_En_Cons_BLR_3 Sp_En_BO_7104D → Spec_En_Cons_BLR_4 Sp_En_BO_7104E → Spec_En_Cons_BLR_5 |
| Known bug | Alias map is currently hardcoded. It should be driven by a pi_alias column in the tag table. (See GenAI opportunity below.) |

### CCP Quality Check — 4 embedded quality nodes

These four nodes run immediately after fetch_pi_data and before any formula evaluation. They validate the 107 most critical tags using rules from the case_configuration_portal table.

| Node | What it checks | Switch code logic | Nov 2024 result |
| --- | --- | --- | --- |
| check_tag_nan | Any tag value is NaN / missing | nan_switch = 14 → replace with default_value and log nan_switch = 16 → replace silently | 0 NaN issues detected |
| check_tag_out_of_bound | Value outside [LOLO, HIHI] bounds Example: Spec_En_Cons_BLR_1 LOLO = 0, HIHI = 3.5 GJ/t | oob_switch = 4 → replace with default_value oob_switch = 3 → warn only | 3 OOB issues, all corrected with default values |
| check_tag_stuck | Same value for N consecutive hours | Requires time-series window (last N rows) Demo: returns empty — production only | 0 stuck issues (demo stub) |
| apply_defaults | Consolidate all issue corrections | Merge all issue lists into final validated snapshot | Final snapshot: 437 tags, 3 corrected |

| DATA | Sample PI tag values from Nov 2024 snapshot |
| --- | --- |

| PI Tag Name | PI Address | Value | Unit | Description |
| --- | --- | --- | --- | --- |
| VHP_Steam_Pressure | UN.ETH.17PC7032.PV | 102.51 | bar g | Very High Pressure Steam |
| VHP_Steam_Temperature | UN.ETH.12TI2107.PV | 494.80 | °C | VHP Steam Temperature |
| HP_Steam_Pressure | UN.UO.70PI0012A.PV | 44.76 | bar g | High Pressure Steam |
| HP_Steam_Temperature | UN.UO.70TI0007.PV | 398.54 | °C | HP Steam Temperature |
| BLR_1_HPS_Gen_raw | UN.UO.71FI1012A.PV | 79,100 | kg/h | Boiler 1 HP Steam output (raw) |
| BLR_1_Status | UN.UO.71DI1001.PV | 1 | on/off | Boiler 1 Running Status |
| Spec_En_Cons_BLR_1 | Sp_En_BO_7104A | 2.856 | GJ/t | Boiler 1 Specific Energy Consumption |
| DMW_Makeup | UN.UO.71FI2001.PV | 178.58 | t/h | Demineralised Water Makeup |
| Air_Compressor_Motor_B_Power | UN.UO.72PI2101.PV | 1.25 | MW | Air Compressor B Motor Power |
| EOEG_1_HPS_Demand | UN.EG1.90FI101.PV | 2.009 | t/h | EG Plant 1 HP Steam Demand |

| GenAI | Integration opportunities in this block |
| --- | --- |

| 🤖 | GenAI Opportunity: Auto-generate alias map from PI tag descriptions |
| --- | --- |
|  | Problem: standardize_columns() currently has 5 hardcoded aliases. In production, hundreds of tags may have |
|  | PI-native names that differ from the feature file canonical names. Manually maintaining this list is error-prone. |
|  | Solution: Use an LLM to match PI tag descriptions to feature file tag descriptions semantically. |
|  | Prompt pattern: |
|  | "Given these PI tags with descriptions: [...] and these feature file tag names with descriptions: [...] |
|  | Generate a JSON alias map where the PI name maps to the canonical feature file name. |
|  | Only map where you are confident the semantic meaning is the same." |
|  | Engineer reviews the LLM output before committing to the config — GenAI suggests, human approves. |
|  | This is the "GenAI Needs Human Gates" golden rule from the blueprint. |

| 🤖 | GenAI Opportunity: Intelligent CCP default value recommendation |
| --- | --- |
|  | Problem: For each of the 107 CCP tags, an engineer must manually choose the default_value |
|  | to substitute when a sensor goes bad. This is currently set to a fixed engineering judgment value. |
|  | Solution: Use an LLM + historical PI data to recommend context-aware defaults. |
|  | Approach: |
|  | 1. Pull last 30 days of PI data for the tag. |
|  | 2. Compute: median, mode, 5th/95th percentile, time-of-day pattern. |
|  | 3. Feed summary statistics + tag description to an LLM. |
|  | 4. LLM recommends a default and explains its reasoning. |
|  | 5. Engineer reviews and approves. |
|  | This turns a static default into a data-driven recommendation updated each month. |

| 🤖 | GenAI Opportunity: Natural language query over PI data |
| --- | --- |
|  | Problem: Engineers must know exact tag names to query the PI historian. |
|  | "Show me boiler efficiency when LP steam pressure is above 5.5 bar" requires knowing |
|  | the exact tag names for efficiency and LP pressure. |
|  | Solution: A GenAI layer that translates natural language into PI queries. |
|  | User: "Why was total HP steam generation higher than usual last Tuesday morning?" |
|  | LLM: Identifies relevant tags → builds PI Web API query → retrieves data → explains anomaly. |
|  | This is a standard RAG (Retrieval-Augmented Generation) pattern with the tag table as the knowledge base. |

# Block 2 — Inferred Tag Calculation Engine

Micro-pipeline: inferred_engine/nodes.py  |  Kedro stage 03 of 08

## 2.1  What Is an Inferred Tag and Why Do We Need This Block?

Of the 3,761 tags in the feature file, 2,862 are inferred — they have no PI sensor address. They are calculated quantities: sums, ratios, polynomial curve fits, status flags, enthalpy values, cost components. The optimizer cannot run without them because the objective function and constraints reference inferred tags, not raw PI readings.

Examples of what inferred tags represent:

- BLR_1_HPS_Gen = BLR_1_HPS_Gen_raw / 1000  →  Converts raw kg/h PI reading to t/h used in all formulas

- Total_BLR_HPS_Generation = Σ(BLR_x_HPS_Gen × BLR_x_Status)  →  Total HP steam output across all running boilers

- HP_Steam_Enthalpy = polynomial(HP_Steam_Pressure, HP_Steam_Temperature)  →  Thermodynamic property for letdown energy balance

- ETH_Plant_Status = if(Total_Ethylene_Load > 100, 1, 0)  →  Is the Ethylene plant running?

- Objective_2 = Power_cost + Fuel_cost + DMW_cost  →  The number the optimizer minimises

The challenge is that these 2,862 formulas are not independent. They form a directed dependency graph. Evaluating them in the wrong order produces wrong results. This block builds the graph, determines the correct evaluation order, handles circular references, and evaluates all formulas.

| INPUT | What goes into this block |
| --- | --- |

| Input | Source | Format | Key content |
| --- | --- | --- | --- |
| ctx_actual | Output of Block 1 + sub-models | Dict[str, float] ~3,300 entries before inferred | PI tag values + aliases + sub-model outputs. This is the starting context that formulas pull from. |
| inferred_details table | EO_UN_FF_Rev_14.xlsx sheet: inferred_details | 2,863 rows Columns: tag_name, formula_expression | 2,863 formula strings such as: "[BLR_1_HPS_Gen_raw]/1000" "([Total_Power_for_Drives]+[Power_Consumption_Plant_U_O]) × 3.6 × [Power_Rate]" |
| inferred_tag_rm_block_mapping | EO_UN_FF_Rev_14.xlsx sheet: inferred_tag_rm_block_mapping | 2,850 rows | Maps each inferred tag to its processing rm_block (e.g. data_enrichment_inferred_calculation) |

| OUTPUT | What comes out of this block |
| --- | --- |

| Output | Format | Size (Nov 2024) | What it represents |
| --- | --- | --- | --- |
| ctx_inferred | Dict[str, float] | ~5,700 entries (2,239 new tag + _actual pairs) | Full evaluation context: every PI tag + every successfully evaluated inferred tag, each stored as both tag_name and tag_name_actual |
| n_evaluated | int | 2,239 | Count of inferred tags that evaluated to a non-NaN value. 624 tags returned NaN because their upstream PI tags were not in the demo subset. |
| circular_tags (resolved) | List[str] | 13 tags | 13 tags involved in mutual circular dependencies — solved via scipy.fsolve and injected back into context before the DAG evaluation |
| DAG object (G) | nx.DiGraph | 3,666 nodes 7,453 edges | The full dependency graph. Can be visualized, audited, or exported for debugging. |

Sample inferred tag values computed in the Nov 2024 run:

| Inferred Tag | Formula (abbreviated) | Computed Value | Meaning |
| --- | --- | --- | --- |
| BLR_1_HPS_Gen | [BLR_1_HPS_Gen_raw] / 1000 | 79.10 t/h | Boiler 1 HP steam output |
| BLR_2_HPS_Gen | [BLR_2_HPS_Gen_raw] / 1000 | 80.23 t/h | Boiler 2 HP steam output |
| BLR_3_HPS_Gen | [BLR_3_HPS_Gen_raw] / 1000 | 80.03 t/h | Boiler 3 HP steam output |
| BLR_4_HPS_Gen | [BLR_4_HPS_Gen_raw] / 1000 | 80.73 t/h | Boiler 4 HP steam output |
| BLR_5_HPS_Gen | [BLR_5_HPS_Gen_raw] / 1000 | 79.54 t/h | Boiler 5 HP steam output |
| Total_BLR_HPS_Generation | Σ(BLR_x_HPS_Gen × BLR_x_Status) | 399.63 t/h | Total HP steam across all ON boilers |
| HP_Steam_Enthalpy | polynomial(P, T) | 521.96 kcal/kg | Thermodynamic enthalpy at HP conditions |
| Fuel_Bill | Total_Fuel × LHV × Fuel_Rate | ~1,339 $/hr | Hourly fuel cost (from boilers) |
| Objective_2 | Power + Fuel + DMW cost | ~1,715 $/hr | Total operating cost — what the optimizer minimizes |

| CODE | The five Kedro nodes — how they work |
| --- | --- |

### Shared Utility: safe_eval_expr (the formula engine)

Before the five nodes, this shared utility function is defined. It is the single most important function in the entire pipeline — every formula evaluation in every stage passes through it.

| Property | Detail |
| --- | --- |
| Function signature | safe_eval_expr(expr: str, ctx: Dict[str, float]) → float |
| Step 1 — bracket replacement | Replace [Tag_Name] references with ctx values. Example: [BLR_1_HPS_Gen_raw] → "79100.0" Tries: tag_actual → tag_optimum → tag (bare name) |
| Step 2 — identifier substitution | Replace bare tag names in the expression with their values. Sorted longest-first to prevent partial matches (e.g. "Total_BLR_HPS" must not match "BLR_HPS" partially) |
| Step 3 — syntax conversion | Convert domain syntax to Python: if(cond, a, b) → (a if cond else b) && → and, ¦¦ → or, ceiling() → math.ceil() |
| Step 4 — restricted eval | eval() with no __builtins__, only safe math namespace: {abs, min, max, sum, round, ceil, floor, sqrt, exp, log, nan, inf} |
| Error handling | Returns np.nan on ANY exception — never raises, never corrupts context. A bad formula in one tag does not stop 2,862 others from evaluating. |
| Formula complexity handled | 136 pure constants (e.g. "2.04") ¦ 110 single tag refs ¦ 490 conditionals 162 polynomial (^ operator) ¦ 81 formulas with 10+ dependencies |

### Node 1/5 — build_dependency_graph

| Property | Detail |
| --- | --- |
| Function signature | build_dependency_graph(inferred_df: pd.DataFrame) → nx.DiGraph |
| What it does | Scans all 2,863 formula strings for [Tag_Name] references. For each reference found, adds a directed edge: dependency → tag. Result: a directed graph where an edge A → B means "B depends on A" |
| Key implementation | Uses re.findall(r"\[([^\]]+)\]", formula) to extract all [Tag] refs. Strips _actual/_optimum suffixes before adding edges (they refer to the same tag). Result: 3,666 nodes, 7,453 dependency edges |
| Why NetworkX? | Built-in algorithms: topological_sort, simple_cycles, is_directed_acyclic_graph. No need to implement graph algorithms from scratch. |
| Nov 2024 stats | 3,666 nodes (unique tag names appearing in formulas) 7,453 directed dependency edges Build time: < 1 second |

### Node 2/5 — detect_circular_refs

| Property | Detail |
| --- | --- |
| Function signature | detect_circular_refs(G: nx.DiGraph) → List[str] |
| What it does | Finds all tags involved in circular dependencies using nx.simple_cycles(). Example: Tag A formula references Tag B, Tag B formula references Tag A. Both A and B are in a cycle — both are returned. |
| Nov 2024 result | 13 circular tags detected across multiple mutual dependency pairs |
| Why does this happen? | Certain steam system quantities are genuinely interdependent: Steam enthalpy depends on conditions; conditions depend on flow; flow depends on enthalpy. The physics has no clean ordering. |
| What happens to them? | Circular tags are excluded from the DAG topological sort. They are sent to the fixed_point_iteration node for simultaneous solution. |

### Node 3/5 — topological_sort_tags

| Property | Detail |
| --- | --- |
| Function signature | topological_sort_tags(G: nx.DiGraph, circular_tags: List[str]) → List[str] |
| What it does | Removes the 13 circular tags from the DAG copy. Validates the remaining graph is truly acyclic: nx.is_directed_acyclic_graph(dag). Runs nx.topological_sort(dag) → ordered list where every tag appears after all its dependencies. |
| Nov 2024 result | 3,653 tags in topological order (3,666 − 13 circular) This is the evaluation sequence fed to evaluate_inferred_tags |
| Key guarantee | When evaluate_inferred_tags processes BLR_1_HPS_Gen (which depends on BLR_1_HPS_Gen_raw), the raw PI value is already in ctx. When it processes Total_BLR_HPS_Generation, all five individual BLR_x_HPS_Gen values are already computed. This is guaranteed by the sort. |

### Node 4/5 — run_fixed_point_iteration

| Property | Detail |
| --- | --- |
| Function signature | run_fixed_point_iteration(ctx, circular_tags, inferred_df) → Dict |
| What it does | Builds a system of equations from the 13 circular tags. Uses scipy.fsolve (Newton-based solver) to find values where all equations are simultaneously satisfied. Injects the solution back into ctx before DAG evaluation. |
| Math behind it | residuals(x) = [safe_eval_expr(formula_i, ctx_with_x) - x_i for each circular tag i] fsolve finds x where residuals = 0, i.e. where each tag's formula output equals its assumed value. This is the definition of a self-consistent fixed point. |
| Initial guess | Uses current ctx values as x0 — typically already near the solution since PI data is consistent. |
| Why not iterate? | Naive iteration (evaluate A from B, then B from A, repeat until converged) may diverge or require many iterations. fsolve converges in few Newton steps. |

### Node 5/5 — evaluate_inferred_tags

| Property | Detail |
| --- | --- |
| Function signature | evaluate_inferred_tags(ctx, inferred_df, order) → Tuple[Dict, int] |
| What it does | Iterates through the topological order list (3,653 tags). For each tag, calls safe_eval_expr(formula, ctx). If result is not NaN, writes it to ctx as both tag_name and tag_name_actual. If result is NaN (missing dependency), skips silently — does not block other tags. |
| Why _actual suffix? | Post-optimisation, the context holds BOTH actual and optimum values. Formulas referencing [Tag_Name_actual] get the actual value. Formulas referencing [Tag_Name_optimum] get the optimised value. This enables the benefit and opportunity calculations in stage 07. |
| Nov 2024 result | 2,239 tags evaluated successfully (non-NaN) 624 returned NaN due to missing upstream PI tags (Would be 2,863/2,863 with full PI Web API connection) |
| Processing pattern | Formula type breakdown: 136 constants → trivially fast 490 conditionals (if statements) → boolean logic 162 polynomial expressions (^ operator) → curve-fit evaluations 419 formulas with 5+ tag dependencies → multi-tag calculations |

| DAG | How the dependency graph looks |
| --- | --- |

The dependency graph for the Nov 2024 run has 3,666 nodes and 7,453 edges. Conceptually it has three layers:

| Layer | What it contains | Example tags | Evaluation order |
| --- | --- | --- | --- |
| Layer 1 — Roots (no dependencies) | Tags whose formulas are pure constants or reference only PI tags directly | BLR_1_HPS_Gen_raw → BLR_1_HPS_Gen HP_Steam_Pressure (PI) → HP_Steam_Enthalpy Fuel_Rate = 1.185 (constant) | First — PI tags are already in ctx |
| Layer 2 — Derived (1–2 hops from PI) | Tags that depend on layer 1 outputs Single-step calculations | BLR_1_HPS_Gen Fuel_BLR_1 Plant status flags Boiler efficiency tags | Second — after layer 1 |
| Layer 3 — Aggregates (multi-hop) | Tags that aggregate across multiple layer 2 tags Often the quantities the optimizer actually needs | Total_BLR_HPS_Generation HP_Steam_Consumption Fuel_Bill, Power_Bill, DMW_Bill Objective_2 | Last — depends on everything above |
| Circular group (fsolve) | 13 tags with mutual dependencies Removed from DAG, solved separately | Steam enthalpy ↔ steam condition pairs in the letdown and deaerator circuits | Before DAG — results injected as layer 1 |

| GenAI | Integration opportunities in this block |
| --- | --- |

| 🤖 | GenAI Opportunity: LLM-assisted formula authoring and validation |
| --- | --- |
|  | Problem: Writing 2,863 formula expressions correctly requires deep domain knowledge and is highly error-prone. |
|  | A typo in [BLR_1_HPS_Gen_rwa] silently returns 0 instead of 79 t/h. |
|  | Solution 1 — Formula generation from description: |
|  | Engineer writes: "Calculate total HP steam generated by all running boilers" |
|  | LLM suggests: "([BLR_1_HPS_Gen]*[BLR_1_Status] + [BLR_2_HPS_Gen]*[BLR_2_Status] + ...)" |
|  | Engineer validates against known physics before committing to the feature file. |
|  | Solution 2 — Formula validation: |
|  | Feed formula string + list of available PI tags to an LLM. |
|  | LLM identifies: "Tag [BLR_1_HPS_Gen_rwa] is not in the tag registry — did you mean [BLR_1_HPS_Gen_raw]?" |
|  | Catches typos before the formula reaches production. |

| 🤖 | GenAI Opportunity: Automatic DAG anomaly detection |
| --- | --- |
|  | Problem: When a new formula is added to the feature file, an engineer must manually check that it does not |
|  | create an unexpected new circular dependency or an excessively deep dependency chain. |
|  | Solution: GenAI-assisted DAG analysis report. |
|  | After any feature file update, run: |
|  | 1. Rebuild the DAG. |
|  | 2. Send the diff (new/changed nodes and edges) to an LLM. |
|  | 3. LLM reports: "New tag X creates a cycle with Y and Z — here is the dependency path." |
|  | "Tag W now has 47 upstream dependencies — this may slow evaluation significantly." |
|  | "Tag V changed from 2 to 8 dependencies — verify this is intentional." |
|  | This turns a static engineering review into an automated continuous check. |

| 🤖 | GenAI Opportunity: Smart imputation for NaN inferred tags |
| --- | --- |
|  | Problem: 624 of 2,863 inferred tags returned NaN in the demo because their upstream PI tags are missing. |
|  | In production, PI sensor faults cause the same problem mid-shift. |
|  | Solution: LLM + ML hybrid imputation. |
|  | When an inferred tag returns NaN: |
|  | 1. Identify which upstream PI tags caused the NaN (trace the DAG backwards). |
|  | 2. Use a LightGBM model (trained on 6 months of historical PI data) to estimate the missing PI tag value. |
|  | 3. Use an LLM to explain the imputation to the operator: |
|  | "BLR_3_HPS_Gen_raw is unavailable. Based on current fuel flow and historical efficiency, |
|  | estimated output is 78.5 t/h. Confidence: high. Last reliable reading: 2 hours ago." |
|  | The rm_block table already has an entry: data_enrichment_pi_tag_imputation — this is where this fits. |

| 🤖 | GenAI Opportunity: Conversational formula explainer for operators |
| --- | --- |
|  | Problem: Operators see a tag value change (e.g. Objective_2 increases from $1,680 to $1,850/hr) but cannot |
|  | easily trace which upstream tag caused it without understanding 2,863 formula dependencies. |
|  | Solution: A GenAI "explain this tag" feature. |
|  | Operator asks: "Why did Objective_2 go up by $170/hr in the last hour?" |
|  | System: |
|  | 1. Computes the contribution of each term in the Objective_2 formula. |
|  | 2. Traces the largest contributor back through the DAG to its root PI tag. |
|  | 3. LLM generates: "The increase is driven by higher fuel consumption in Boiler 3. |
|  | Fuel_BLR_3 increased from 2.8 to 3.3 GJ/h, likely because BLR_3_HPS_Gen_raw rose |
|  | from 78 to 92 t/h following a step-up in EOEG-3 steam demand at 14:00." |
|  | Turns the DAG into an interactive root-cause analysis tool. |

# Combined Data Flow: Block 1 → Block 2

| Step | Block | Node | ctx size | What happened |
| --- | --- | --- | --- | --- |
| 1 | Block 1 | create_pi_connection | 0 | PI historian connection established (mock in demo) |
| 2 | Block 1 | fetch_pi_data | 0 | EO_input_data.xlsx loaded: 4,320 rows × 438 cols. Latest row selected: 2024-11-29 00:00:00 |
| 3 | Block 1 | standardize_columns | 0 | 5 boiler SpEn tags renamed: Sp_En_BO_7104A → Spec_En_Cons_BLR_1 (etc.) |
| 4 | Block 1 | check_tag_nan | 0 | 107 tags checked for NaN. 0 NaN issues. |
| 5 | Block 1 | check_tag_out_of_bound | 0 | 107 tags checked against LOLO/HIHI. 3 OOB issues corrected with defaults. |
| 6 | Block 1 | build_eval_context | 874 | 437 PI tags written as tag + tag_actual. ctx now has 874 entries. |
| 7 | Block 2 | build_dependency_graph | 874 | 2,863 formulas scanned. 3,666 node DAG with 7,453 edges constructed. |
| 8 | Block 2 | detect_circular_refs | 874 | 13 circular tags identified using nx.simple_cycles(). |
| 9 | Block 2 | topological_sort_tags | 874 | 13 circular tags removed. Remaining 3,653 sorted topologically. |
| 10 | Block 2 | run_fixed_point_iteration | 900 | 13 circular tags solved via scipy.fsolve. Their values added to ctx. |
| 11 | Block 2 | evaluate_inferred_tags | ~5,700 | 3,653 formulas evaluated in order. 2,239 succeeded. 624 returned NaN (missing PI upstream). |

What the next pipeline stages consume from Block 2 output

Stage 04 Sub-Models: ctx_inferred is passed as input. Sub-models compute plant status flags and composite demands.

Stage 05 Opt Prep: ctx_inferred feeds the bound evaluation for all 141 optimizer variables.

Stage 06 Optimizer: ctx_inferred is the starting point. The optimizer queries Objective_2 for every candidate solution.

Stage 07 Post-Opt: ctx_inferred_actual is merged with ctx_optimum. Post-opt formulas reference both.

Stage 08 ODS/SEU: 115 cause expressions and 57 SEU expressions all evaluated against the merged context.

Every single downstream stage depends on the correctness and completeness of Block 2 output.

A missing or wrong inferred tag propagates silently — this is why the NaN-tracking and

DAG-order guarantees in this block are critical.